## Est
CHAMUNDESWARI ELECTRICITY SUPPLY COMPANY LIMITED
Estimate No : SOK- Date:
Estimate for providing Electrical infrastructure for the newly developed residential layout in fovour of Smt.Lakshmishivakumar Sy No-43/1 at Gejjagalli Village limits (Mandakalli Survey Number) Kasaba Hobli, Mysuru(Tq), pertains to O&M Kadakola Section, Chamundipuram Sub-division. | [7 empty] | 440
"UNDER SELF- EXECUTION BASIS" | [7 empty] | 293.3333
PART-A : Extension of Primary Line | [7 empty] | 345.098
Sl. NO | Details of materials | Units | Qty | Materials |  | Labour
|  |  |  | Rate | Amount | Rate | Amount
1 | RCC DP Structure using 9 Mtrs RCC Pole with WL 145 kg | Set's. | 0 | 56654 | 0 | 9182 | 0
2 | Pre-Stressed Tubular Spun Pole 11M Long | No's. | 1 | 17702 | 17702 | 4449 | 4449
| a) Base concreting 1:4:8, 1000x1000x150mm | each | 1 | 0 | 0 | 936 | 936
| b) Pole concreting 1:2:4, 1000x1000x2500 mm | each | 1 | 0 | 0 | 15608 | 15608
| c) Coping 1:2:4 (as per actuals) | each | 1 | 0 | 0 | 2372 | 2372
3 | Single H Frame without Transformer Seating and Seating angle support X arm for 11 mtr Spun Pole-GI | Set | 1 | 17987 | 17987 | 2703 | 2703
4 | 11kV, 200Amps, Single Break GOS | No's | 1 | 9450 | 9450 | 1104 | 1104
5 | 9 Mtrs Long RCC Pole | No's. | 6 | 7076 | 42456 | 1742 | 10452
| Base concreting 1:4:8, 500x650x150 mm | No's. | 6 | 0 | 0 | 312 | 1872
6 | 9 Mtrs Long RCC Pole for Strut | No's. | 0 | 7076 | 0 | 1742 | 0
7 | Earthing materials pipe type for grounding | Set of 3 Nos | 1 | 1729 | 1729 | 949 | 949
8 | Spiral earth electrode | Set's. | 7 | 239 | 1673 | 93 | 651
9 | Special cross arm with cross arm for EG Stirrups,braces, clamps, bolts nuts and washers complete. GI | Set's. | 2 | 1434 | 2868 | 463 | 926
10 | 11 kV, Horizontal Cross Arm with HT Single Top supports, clamps, bolts, nuts & washers - GI for RCC Pole - 9 Mtr Long, 145 Kg WL | Set's. | 9 | 850 | 7650 | 272 | 2448
11 | 11KV 45 KN Polymeric Insulator | No's. | 9 | 186 | 1674 | 0 | 0
12 | 11 KV, 5KN composite / polymeric Pin Insulator (24mm dia FP rod) | No's. | 24 | 205 | 4920 | 0 | 0
13 | Rabbit conductor with 1.5% sag | KM's. | 0.41 | 46234 | 18955.94 | 4361 | 1788.01
| conductor accessories @ 3% |  |  |  | 568.6782
14 | PG Clamps for Rabbit conductor | No's. | 24 | 102 | 2448 | 0 | 0
15 | Caution/Danger Board | No's | 1 | 150 | 150 | 80 | 80
16 | Guarding between HT&LT line/Road guarding (including Xarm ,clamp & B&N) | Span | 6 | 4650 | 27900 | 1804 | 10824
17 | 4 Pin Cross Arm with clamps, bolts, nuts and washers for guarding | Set | 8 | 420 | 3360 | 160 | 1280
18 | 1.1 kV Polymeric Pin Insulator | No's | 0 | 87 | 0 | 0 | 0
19 | Guy set complete for HT | Set's. | 1 | 1170 | 1170 | 593 | 593
20 | Concreting materials for guy sets without cement. | Set's. | 1 | 0 | 0 | 250 | 250
21 | Fish Plate with necessary Clamps, bolts & nuts etc complete. | No's. | 0 | 264 | 0 | 122 | 0
22 | Transparent Alkathine tube 19mm dia, 2mm thick in coils of 30 mtrs | Coil | 1 | 517 | 517 | 0 | 0
23 | Miscellanius materilas & labour |  |  |  | 321.38 |  | 214.99
| Total material / Labour cost |  |  |  | 163499.9982 |  | 59500
1 | MATERIAL COST (Execlusive of 18% GST) |  |  | 163499.9982
2 | LABOUR COST (Execlusive of 18% GST) |  |  | 59500
3 | Basic Rate (Sum of Sl No. 1 & 2) |  |  | 222999.9982
4 | Area Specific Loading on Basic Rates (Sl No. 3) wherever applicable |  | 0% | 0
5 | Applicable 18% GST on Sum of Sl No. 3 & 4 |  |  | 40139.9997
6 | Cost of Estimate (Sum of Sl No. 3 to 5) |  |  | 263139.9979
7 | Government Electric Inspectorate Charges @ Rs.1000/- per KM(Route length) | Kms | 0.13 | 1000
8 | Total Cost of Estimate (Sum of Sl No. 6 & 7) |  |  | 264139.9979
PART - B-1 : Providing DTC((Excluding Transformer) Matireals taken as per field condition & Rates taken from CDS-26)
Sl. NO | Details of materials | Units | Qty | Materials |  | Labour
|  |  |  | Rate | Amount | Rate | Amount
1 | 9 Mtr RCC DP Transformer Structure (Using 9 Mtr RCC Poles). | No's. | 1 | 31554 | 31554 | 6983 | 6983
2 | 11 KV, 5KN Polymeric Pin Insulator (24mm Dia FRP Rod). | Set's. | 3 | 205 | 615 | 0 | 0
3 | 11KV 45 KN Polymeric Insulator. | Set's. | 3 | 186 | 558 | 0 | 0
4 | Guy Set Complete with No.15 strain insulator & Concreting materials. | Set's. | 4 | 1170 | 4680 | 593 | 2372
5 | Guy concreting with Boulders, Mud and Sand | Set's. | 4 | 0 | 0 | 250 | 1000
6 | GI Wire 8 SWG | Kg's. | 5 | 75.04 | 375.2 | 0 | 0
7 | Guy Wire 7/10 SWG | Kg's. | 10 | 77.23 | 772.3 | 0 | 0
8 | Miscellanius materilas & labour |  |  |  | 445.5 |  | 145
| Total material / Labour cost |  |  |  | 39000 |  | 10500
1 | MATERIAL COST (Execlusive of 18% GST) |  |  | 39000
2 | LABOUR COST (Execlusive of 18% GST) |  |  | 10500
3 | Basic Rate (Sum of Sl No. 1 & 2) |  |  | 49500
4 | Area Specific Loading on Basic Rates (Sl No. 3) wherever applicable |  | 0% | 0
5 | Applicable 18% GST on Sum of Sl No. 3 & 4 |  |  | 8910
6 | Cost of Estimate (Sum of Sl No. 3 to 5) |  |  | 58410
7 | Government Electric Inspectorate Charges |  |  | 0
8 | Total Cost of Estimate (Sum of Sl No. 6 & 7) |  |  | 58410
PART - B-2 : Erection of 3 Phase, 11kV/433 V, 100kVA BEE – 5 Star Rated Distribution Transformer Centre (Including Transformer as per CDS-26) Under DCW
Sl. NO | Details of materials | Units | Qty | Materials |  | Labour
|  |  |  | Rate | Amount | Rate | Amount
1 | 11kV/433V, 100kVA, 3 Phase 50 Cys Distribution Transformer BEE - 5 Star Rated with Oil | No's | 1 | 221952 | 221952 | 1590 | 1590
2 | Earthing materials pipe type for grounding | Set of 3 Nos | 3 | 1729 | 5187 | 949 | 2847
3 | Caution/Danger Board | No's | 1 | 150 | 150 | 80 | 80
4 | Anti Climbing Device (12mtrs GI Barbed Wire) | Kg's | 2 | 89 | 178 | 42 | 84
5 | 11kV Lightning Arester, Metal Oxide 9kV, 5kA Polymetic Type with ground disconnector | Set of 3 Nos | 1 | 4752 | 4752 | 119 | 119
6 | LT Distribution Box for 100kVA with MCCB | No's | 1 | 22686 | 22686 | 385 | 385
7 | LT Wiring (From DTC to LT Line via Metering Box & LT Protection Kit) SINGLE CIRCUIT
| i. Al Lead Wire - 120 Sqmm | Mtrs | 45 | 143.19 | 6443.55 | 949 | 949
| ii. Copper lugs - 120 Sqmm | Nos | 12 | 140 | 1680
| iii. PG Clamps - Rabbit to 120 Sqmm | Nos | 4 | 273 | 1092
| iv. Spacers for DTC Wiring | Nos | 8 | 42 | 336
| v. Fish Plate with necessary Clamps,bolts & nuts etc complete (Galvanised) | No's | 2 | 264 | 528
8 | LT Metering box with CTs and necessary wiring for housing ETV Meter. | No's | 1 | 5126 | 5126 | 865 | 865
9 | LT Electronic Tri-Vector Meter 5A, Class-0.5/1.0 accuracy. | No's | 1 | 3396 | 3396 | 480 | 480
10 | 11kV Solid Core Type HG Fuse Unit | Set's/3no's | 1 | 1069 | 1069 | 237 | 237
11 | 11kV, 200Amps, Single Break GOS | No's | 1 | 9450 | 9450 | 1104 | 1104
12 | Modem | No's | 1 | 14415 | 14415 | 1346 | 1346
13 | Miscellanius materilas & labour |  |  |  | 559.45 |  | 414
| Total material / Labour cost |  |  |  | 299000 |  | 10500
1a | Material Cost (Execlusive of 18% GST) Material Supplied by ESCOMs |  |  | 299000
2a | Labour Cost (Execlusive of 18% GST) Carried out by ESCOMs employees |  |  | 10500
| 21% of overhead Charges & Contractor's profit deloaded on Material Cost. |  |  | 236210
| 21% of overhead Charges & Contractor's profit deloaded on Labour Charges. |  |  | 8295
1b | Material Cost (Execlusive of 18% GST) Material Supplied by Agency |  |  | 0
2b | Labour Cost (Execlusive of 18% GST) Carried out by agency |  |  | 0
3 | Basic Rate (Sum of Sl No. 1a, 1b, 2a & 2b) |  |  | 244505
4 | Area Specific Loading on Basic Rates (Sl No. 3) wherever applicable |  | 0% | 0
5 | Applicable 18% GST on Sum of Sl No. 3 & 4 |  |  | 44010.9
6 | Cost of Estimate (Sum of Sl No. 3 to 5) (Amount Put To Tender) |  |  | 288515.9
7 | Government Electric Inspectorate Charges @ Rs.3500/- per DTC | No's | 1 | 3500
8 | Total Cost of Estimate (Sum of Sl No. 6 & 7) |  |  | 292015.9
PART - C : Extension of 3 phase 5 wire secondary circuit with in the Layout.
Sl. NO | Details of materials | Units | Qty | Materials |  | Labour
|  |  |  | Rate | Amount | Rate | Amount
1 | Pre-Stressed Tubular Spun Pole 11M Long | No's. | 0 | 17702 | 0 | 4449 | 0
| a) Base concreting 1:4:8, 1000x1000x150mm | each | 0 | 0 | 0 | 936 | 0
| b) Pole concreting 1:2:4, 1000x1000x2500 mm | each | 0 | 0 | 0 | 15608 | 0
| c) Coping 1:2:4 (as per actuals) | each | 0 | 0 | 0 | 2372 | 0
2 | 9 Mtrs Long RCC Pole | No's | 2 | 7076 | 14152 | 1742 | 3484
3 | 9 Mtrs Long RCC Pole for stud | No's | 0 | 7076 | 0 | 1742 | 0
| Base concreting 1:4:8, 500x650x150 mm | No's | 2 | 0 | 0 | 312 | 624
4 | Spiral earth electrode | Set's. | 2 | 239 | 478 | 93 | 186
5 | LT 4 Pin Cross Arm with clamps, bolts, nuts & washers with brace - GI | Set's | 9 | 554 | 4986 | 160 | 1440
6 | LT 2 Pin Aross Arm with clamps, bolts, nuts & washers with braces - GI | Set's | 9 | 348 | 3132 | 160 | 1440
7 | 2-Pin cross arm/ Fish plate for stud pole | Set's | 0 | 266 | 0 | 160 | 0
8 | No.8 Strain Insulator | No's | 20 | 27 | 540 | 0 | 0
9 | 1.1 kV Polymeric Pin Insulator | No's | 25 | 87 | 2175 | 0 | 0
10 | Rabbit Conductor | KM's. | 0.72 | 46234 | 33288.48 | 4361 | 3139.92
| Conductor Accessories@3% |  |  |  | 998.6544 | 0 | 0
11 | Guy set complete for LT | Set's | 1 | 1138 | 1138 | 593 | 593
12 | Concreting materials for guy sets without cement | Set's | 1 | 0 | 0 | 250 | 250
13 | Miscellaneous and unforseen materials |  |  |  | 111.87 |  | 343.08
| Total material / Labour cost |  |  |  | 61000.0044 |  | 11500
1 | MATERIAL COST (Execlusive of 18% GST) |  |  | 61000.0044
2 | LABOUR COST (Execlusive of 18% GST) |  |  | 11500
3 | Basic Rate (Sum of Sl No. 1 & 2) |  |  | 72500.0044
4 | Area Specific Loading on Basic Rates (Sl No. 3) wherever applicable |  | 0% | 0
5 | Applicable 18% GST on Sum of Sl No. 3 & 4 |  |  | 13050.0008
6 | Cost of Estimate (Sum of Sl No. 3 to 5) |  |  | 85550.0052
7 | Government Electric Inspectorate Charges @ Rs.500/- per KM(Route length) | Kms | 0.2 | 500
8 | Total Cost of Estimate (Sum of Sl No. 6 & 7) |  |  | 86050.0052
PART - D : Providing LED street light fitting
Sl. NO | Details of materials | Units | Qty | Materials |  | Labour
|  |  |  | Rate | Amount | Rate | Amount
1 | Complete LED (25Watts) fitting with clamp, bend, bracket etc. (As per KPWD Ele SR 2-23-24) | No's | 5 | 2425 | 12125 | 490 | 2450
2 | Sheet Metal/Deep Drawn Street Lighting Metering Box with Automatic Control Swith, | No's | 1 | 5984 | 5984 | 952 | 952
3 | Automatic External switch ON/OFF for street light | No's | 1 | 2303 | 2303 | 0 | 0
4 | PVC Pipe 40MM Dai | Mtrs | 6 | 60 | 360 | 0 | 0
5 | PVC Insulated wire 25 Sq mm single core multi stranded. | Mtrs | 25 | 47.33 | 1183.25 | 0 | 0
6 | Miscellaneous and unforseen materials |  |  |  | 44.75 |  | 98
| Total material / Labour cost |  |  |  | 22000 |  | 3500
1 | MATERIAL COST (Execlusive of 18% GST) |  |  | 22000
2 | LABOUR COST (Execlusive of 18% GST) |  |  | 3500
3 | Basic Rate (Sum of Sl No. 1 & 2) |  |  | 25500
4 | Area Specific Loading on Basic Rates (Sl No. 3) wherever applicable |  | 0% | 0
5 | Applicable 18% GST on Sum of Sl No. 3 & 4 |  |  | 4590
6 | Cost of Estimate (Sum of Sl No. 3 to 5) |  |  | 30090
7 | Government Electric Inspectorate Charges |  |  | 0
8 | Total Cost of Estimate (Sum of Sl No. 6 & 7) |  |  | 30090
ABSTRACT
| PART-A : Extension of primary line |  |  |  | 264139.9979
| PART-B1 : Providing DTC(Excluding Transformer) |  |  |  | 58410
| PART-B2 : Providing DTC(Including Transformer DCW) |  |  |  | 292015.9
| PART-C : Extension of 3 phase 5 wire secondary circuit |  |  |  | 86050.0052
| PART-D : Providing LED street light fitting |  |  |  | 30090
| TOTAL ESTIMATE COST |  |  |  | 730705.9031
CERTIFICATE:
Cerrtifying that I have personaly visited the spot and did the estimate in most economical and safeway to execute the work by using current SR Rate of 2023-24.
| Asst. Executive Engineer (Ele)., |  |  |  | Assistant Engineer (Ele).,
| CESC, O&M, CPM Sub-Divison, |  |  |  | CESC, O&M-Kadakola Section,
| Mysuru. |  |  |  | Mysuru.

## Report
REPORT :
The Estimate amounting Rs.7,30,706.00 is prepared for providing Electrical infrastructure for the newly developed residential layout in fovour of Smt.Lakshmishivakumar Sy No-43/1 at Gejjagalli Village limits (Mandakalli Survey Number) Kasaba Hobli, Mysuru(Tq), pertains to O&M Kadakola Section, Chamundipuram Sub-division.
PART - A : Extension of Primary line
For this, it is proposed to tap the 11kV Gejjagalli NJY feeder, by providing 1 no of 9Mtrs long RCC pole as intermediate at point "A", which is running near to this proposed layout area. Further it is proposed to extend the 11kV HT line to a distanc of 12Mtrs from point "A" to "B", then it is proposed to provide 1no of 11Mtrs long Spun pole with GOS for isolation purpose at the enterance of the layout at Point "B",. Further it is proposed to extend 11kV overhead line with in layout to a distance of 113Mtrs. from point "B" to TC1by using 9Mtrs long RCC poles & Rabbit ACSR conductor with all the associated materials.
The proposed 1Nos of 100 KVA transformers, comes on existing 11kV Gejjagalli NJY feeder fed from 66/11kV Koppaluru-Mandakalli MUSS.
PART - B1&B2 : Providing DTCs
There are 25+1 no of CA sites of different measurement and the total assessed load is 113.73Kw's/89KVA, including water supply and street lights.
The load assessment is made on the following assumption
for sites having 30X40 sq.ft, 30XOdd sq.ft, load calculation sheet enclosed Total 109KW's.
For street light and water supply say, = 1KW +5HP
Total assessed load = 110KW+5HP
Hence, cosidering 90% load on transformer, so 1No's of 100KVA distribution transformer is proposed on double pole transformer structure at location viz., as shown in the sketch.
PART - C : Extension of 3Phase 5wire LT line.
For all the secondary circuits it is also proposed to extend LT 3Phase 5wire line by using 2 no's of 9Mtrs long RCC poles, Rabbit ACSR conductor with all the associated materials.
PART - D : Providing fluoroscent street light fitting
Necessary street light provisions is made in this estimate by using Sheet Metal/Deep Drawn Street Lighting Metering Box with Automatic Control Swith.
ABSTRACT
PART-A : Extension of primary line | 264139.9979
PART-B1 : Providing DTC(Excluding Transformer) | 58410
PART-B2 :Providing DTC(Including Transformer DCW) | 292015.9
PART-C : Extension of 3 phase 5 wire secondary circuit | 86050.0052
PART-D : Providing fluoroscent street light fitting | 30090
TOTAL ESTIMATE COST | 730705.9031
Hence this estimate may kindly sanctioned under Self Execution basis.
Asst. Executive Engineer (Ele)., |  | Assistant Engineer (Ele).,
CESC, O&M, CPM Sub-Divison, |  | CESC, O&M-Kadakola Section,
Mysuru. |  | Mysuru.

## load cal
LOAD ASSESMENT CALCULATION CHART
| 1) | 4KWX24= | 96
| 2) | 6KWX1 = | 6
| 3) | CA site 12.61*28.13 X1 = | 7
|  | Total= | 109KW
|  | Street Light = | 1KW
|  | W/S = | 5HPX746W=3.73KW
|  | Total Load= | 113.73KW
|  | Total Load= | 113.73KW/1.5(Load/DF)=75.82KW
75.82KW/0.85=89.20KVA=89KVA
Total 1X100KVA tr. Is proposed as per KERC
Clause 3.2.1[d] and this Plan is sanctioned by Mysore Urban Development Authority Mysuru.

## load survey
Load calculation sheet for the proposed residential layout developed by Smt.Lakshmishivakumar Sy No-43/1 at Gejjagalli Village limits (Mandakalli Survey Number) Kasaba Hobli, Mysuru(Tq), pertains to O&M Kadakola Section, Chamundipuram Sub-division.
Site No | Measurement in mt |  | Area in sq mt | Area in sq ft | Upto 1200 sq ft 3 KWs | Above 1200 and Up to 2400 sq ft 4 KWs | Above 2400 and Up to 4000 sq ft 6 KWs | Above 4000 sq ft 6 Kw + 1 KW for addl 700 sq ft | Kws reqd /Applied
1 | 14.75 | 16 | 236 | 2539.36 |  |  | 6 |  | 6
2 | 9 | 15.75 | 141.75 | 1525.23 |  | 4 |  |  | 4 | 23.75
3 | 9 | 15.25 | 137.25 | 1476.81 |  | 4 |  |  | 4
4 | 9 | 14.75 | 132.75 | 1428.39 |  | 4 |  |  | 4
5 | 9 | 14.25 | 128.25 | 1379.97 |  | 4 |  |  | 4
6 | 9 | 13.87 | 124.83 | 1343.1708 |  | 4 |  |  | 4
7 | 9 | 13.62 | 122.58 | 1318.9608 |  | 4 |  |  | 4
8 | 9 | 13.42 | 120.78 | 1299.5928 |  | 4 |  |  | 4
9 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
10 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
11 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
12 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
13 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
14 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
15 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
16 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
17 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
18 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
19 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
20 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
21 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
22 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
23 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
24 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
25 | 9 | 12 | 108 | 1162.08 |  | 4 |  |  | 4
CA | 12.61 | 28.13 | 354.7193 | 3816.7797 |  |  |  | 7 | 7 | #REF!
Water supply | [7 empty] | 5 H.P | 3.73 |  |  |  | 75.82
Street light | [8 empty] | 1 |  |  |  | 89.2
Total Kw as per the latest amendment of KERC is 113.73Kws and after taking into consideration of the diversity factor and conversion to Kva the load will be 89KVA | [8 empty] | 113.73
[10 empty] | 9*12 | H | 0.818 |  | 0
[11 empty] | V | 1.09 | 11 | 11.99
[10 empty] | 6.10*9.14 | H |  |  | 0
[11 empty] | V |  |  | 0